The following specification has been developed by: AutoGate, Inc. 7306 Driver Road PO Box 50 Berlin Heights, Ohio 44814 419.588.2796 1.800.944.GATE (4283) www.autogate.com o assist Architects and Designers in the specification of THE SHIELD® ANTI-RAM VEHICLE BARRIERS; security rated vertical pivot (VP) barriers capable of withstanding K4/M30 and K12/M50 vehicle impact in accordance with ASTM F2656-07 and the United States State Departments SD-STD-02.01, REVISION A, DATED MARCH 2003). Anti-Ram Vehicle Barriers are electrically operated vehicle barrier or arms that lift by pivoting vertically at the operator. VP style of operation has advantages over sliding or swinging barriers in the speed of operation and the ability to operate free of road or other obstructions (e.g. snow, ice, curbs, slopes and plant growth). The operator is controlled using low voltage DC power with battery backup allowing operation in the event of utility company power failure. In addition the system is able to be operated in a stand alone mode utilizing solar power cells to maintain battery charge. The systems are furnished as a complete assembly with framing and operator. Pickets or mesh fabric which matches the adjacent fence line can be provided by AutoGate after coordination and approval. Notes to the specifier are included in the boxes. Options that must be selected by the specifier are shown in brackets [ ]. Inapplicable clauses shall be deleted.

SECTION 34 75 13.16 - ANTI-RAM VERTICAL PIVOT ACTIVE BARRIERS

GENERAL

SUMMARY

Section Includes:

Vertically pivoting low voltage electrically operated gates and barriers that are rated to resist penetration of heavily weighted vehicles traveling at a high rate of speed.

Fully welded gate frame with an integral housing which incorporates high strength synthetic ropes that act as the means of capture.

Barrier Arm with gate panel / Barrier Arm with no gate panel solely using an aluminum housing incorporating high strength synthetic ropes.

Barrier operator, of a vertical pivot type, for opening and closing the gate. Security fence panels of [chain link fabric] [vertical pickets] [wire mesh] [matching the contiguous fence line] [custom security materials, pales, etc.]

Tubular steel bolsters at each end of the gate designed to withstand the impact loading of the attacking vehicle.

Coordinate the following with other sections of the specifications to avoid duplication and conflicts.

Concrete and earthwork for operator pads and bolsters.

Bolsters for system operators including foundations.

[Push Button Barrier Controls.]

[Contact Sensing] [and or] [Photoelectric non-contact] external entrapment protection devices including automatic reversing.

Products Not Furnished or Installed under This Section:

Electrical power service to the operator.

Line Fencing.

Passive anti-ram barriers.

[Automatic barrier and gate control systems.]

RELATED SECTIONS

Section [____] - Line fencing.

Section [____] - Earthwork for Foundations.

Section [____] - Cast-In-Place Concrete.

Section [____] - Electrical power and distribution.

REFERENCES

References are listed as a convenience and are often deleted in their entirety. If required by the user agency delete references from the list below that are not actually required by the text of the edited section

American Society for Testing and Materials:  Standard Specifications (ASTM)

ASTM A36/A 36M-08  Standard Specification for Carbon Structural Steel

ASTM A27/A27M-08 Standard Specification for Steel Castings, Carbon, for General Application

ASTM A47/A47M-99(2009) Standard Specification for Ferritic Malleable Iron Castings

ASTM  A53/A53M-07 Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A307-07b Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength

ASTM A500-07  Standard Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes

ASTM A615/A615M-09 Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement

ASTM B221-08 Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes

ASTM B429/B429M-06 Standard Specification for Aluminum-Alloy Extruded Structural Pipe and Tube.

ASTM C33/C33M-08 Standard Specification for Concrete Aggregates.

ASTM C94/C94M-09 Standard Specification for Ready-Mixed Concrete

ASTM C150/C150M-09 Standard Specification for Portland Cement

ASTM F567-07 Standard Practice for Installation of Chain-Link Fence

ASTM F1043-08 Standard Specification for Strength and Protective Coatings on Steel Industrial Chain Link Fence Framework

ASTM F2200-14 Standard Specification for Automated Vehicular Gate Construction.

ASTM F2656-15 Standard Test Method for Vehicle Crash Testing of Perimeter Barriers.

U.S. Army Corp of Engineers – PDC Standard; DOD Certified Anti-Ram Vehicle Barriers.

U.S. Department of State DOS - SD-STD-02.01,RevisionA Test Method for Vehicle Crash Testing of Perimeter Barriers and Gates, 2003

Unified Facilities Criteria (UFC), UFC 4-022-02, Selection & Application of Vehicle Barriers.

Unified Facilities Criteria (UFC) UFC 4-022-01 Army ACP Standard Design and Criteria

National Fire Protection Association (NFPA)

NFPA 70:  National Electrical Code.

Underwriter Laboratories, Inc. (UL)

[Select only if applicable for the project] UL 325 - Standard for Safety for Door, Drapery, Gate,  Louver, and Window Operators and Systems.  Sixth Edition. [Typically not common to crash systems; however, AutoGate is UL 325 listed for this safety standard if desired.  Consult AutoGate.]

PERFORMANCE REQUIREMENT

ASTM F2656-15 test method provides a structured procedure to establish a penetration rating for perimeter barriers subjected to a vehicle impact. The DOS STD STD-02.01 Revision A dated March 2003 is no longer actively used. The DOS Standard has been incorporated into ASTM F2656. As of February 1, 2009, DOS evaluate only new anti-ram barriers tested under ASTM F2656-07 (and later F2656 revisions) Standard Test Method for Vehicle Crash Testing of Perimeter Barriers.

Anti-Ram Vertical Pivot Active Barriers selection shall be based on full scale crash tests conducted in accordance with ASTM F2656 [or] SD-STD-02.01, Revision A March 2003 by an independent test laboratories or government-approved facilities for the following rating:

[Delete if selecting #2 below] DOS K12/ASTM F2656 M50 - Kinetic Energy of approximately 1,200,000 ft-lb (165,960 kg-m) of energy (15,000 lb @ 50 mph [6,818 kg @ 80 kph]).]

[Delete if selecting #1 above] DOS K4/ASTM F2656 M30 - Kinetic Energy of approximately 400,000 ft-lb (55,320 kg-m) of energy, (15,000 lb @ 30 mph [6,818 kg @ 48 kph]).]

Barrier Dimensions[ Each]:

K12/M50 full size gates are available to a clear opening of 15 feet. K12/M50 Barrier Arms are available to a clear opening of 17 feet. K4/M30 gates clear opening of 17 feet, K4/M30 Barrier arms 19 feet. These sizes are subject to standard AutoGate materials. Custom materials from other vendors require consultation with AutoGate for approval or determination to maximum sizes of systems.

Width  (Inside to Inside clear, drivable open between bolsters)- [ _______ feet]  [As indicated ________].

Height (if gate will be needed on Drop Arm) - Operator Pad surface to top of gate [8 feet]  [6 feet] [_______ feet].  [As indicated  ______].

SUBMITTALS

Product Data:  Submit sufficient manufacturer's data to indicate compliance with these specifications.  Mark data to indicate:

Details of material and construction.

Recommended installation requirements to properly accommodate the proposed drop arm/gate and accessories.

Shop Drawings:  Submit shop drawings for fabrication and installation of ornamental metal work.  Include plans, elevations and detail sections.  Indicate materials, methods, finishes and types of joinery, fasteners, anchorages and accessory items.

QUALITY ASSURANCE

Select applicable standards required by the agency operating the facility. Add applicable standard guides or reference documents desired.

Security Barrier Standards:

United States State Departments - SD-STD-02.01, Revision A, dated March 2003

ASTM F2656-15 Standard Test Method for Vehicle Crash Testing of Perimeter Barriers.

United States Department of Defense:

[U.S. Army Corps of Engineers] [Naval Facilities Engineering Command] [Air Force Civil Engineer Support Agency] - Unified Facilities Criteria (UFC)  Security Engineering:  Entry Control Facilities / Access Control Points UFC 4-022-01 25 May 2005

Department of Defense Handbook Selection and Application of Vehicle Barriers MIL-HDBK-1013/14 1 February 1999.

U.S. Army Corp of Engineers – PDC Standard; DOD Certified Anti-Ram Vehicle Barriers.

Federal Emergency Management Agency (FEMA) Risk Management Series - Reference Manual to Mitigate Potential Terrorist Attacks Against Buildings December 2003

SDDCTEA Pamphlet 55-15, TRAFFIC AND SAFETY ENGINEERING FOR BETTER ENTRY CONTROL FACILITIES - 2014.  US Army Military Surface Deployment  and Distribution Command  Transportation Engineering Agency

Vertical Pivot Active Barrier Standards: Comply with requirements of authorities having jurisdiction in Project location. [Note: may not be applicable for all projects, consult AutoGate with any questions]

Operation Control Systems:

UL 325 [Optional and rare for barrier systems, contact AutoGate if you have questions] - Standard for Safety for Door, Drapery, Gate,  Louver, and Window Operators and Systems.

ASTM F2200 - Standard Specification for Automated Vehicular Gate Construction.

Electrical Components, Devices, and Accessories:  NFPA 70, Article 100.

Include the following for Chain Link material or include other infill panels fence standards as applicable

Chain link Standards:

Fencing and Gates: Chain Link Fence Manufacturer's Institute "Specifications for Fence-Posts, Gates and Accessories".  Install in accordance with ASTM F567.

Manufacturer Qualifications:  Minimum three (3) years documented experience producing systems specified in this section.

Installer Qualifications:  An experienced installer with manufacturer factory training or acceptable excavation and installation experience similar in material, design, excavation requirements, and extent to those indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

DELIVERY, STORAGE AND HANDLING

Store components to avoid damage from moisture, abrasion, and other construction activities. Carefully store materials off the ground to provide proper protection against oxidation caused by ground contact.

PROJECT CONDITIONS

Field Measurements:  Take measurements and generate dimensions where Drop Arm and Operator are to be located. Indicate specific location of operator and bolsters with regard to existing roadways, proposed roadways, curb locations, grade changes, elevations, landscaping, adequate overhead clearance for drop arm path, canopies, and buildings.  Coordinate and exchange information with the manufacturer.

COORDINATION AND SEQUENCING

Coordinate system installation with line fencing and paving.  Drop Arm and Operator can be installed independent of paving providing the Operator concrete foundation and its respective bolsters are in place, including electrical control conduits. Upon completion of installation place the Drop Arm in an open position and maintain vertically clear of traffic and surrounding fence line installation.

Operators are designed for 120 volt 15 amp primary service and 24 Volt DC battery back-up (batteries are field supplied and installed).  Installer is to coordinate electrical service with electrical design and electrical trades.  Service connection is supplied via underground conduit and preferably with a GFCI circuit breaker.  Connection is made into a 4” x 4” handy box inside the Operator. Within the box wire GFCI Duplex Receptacle “HOT” off of the main breaker. Receptacle may be used for loads under 15 Amps such as hand tools and the like.

WARRANTY

Standard Warranty:  Provide manufacturer's standard three (3) year warranty against defective materials and workmanship after Date of Substantial Completion.

[Optional, delete if not desired] 2 year Extended Warranty:  Provide an extended manufacturer's warranty for the entire warranty period covering  defective materials and workmanship for the following additional 2 year period beyond the initial three year warranty:

PRODUCTS

ACCEPTABLE MANUFACTURER

AutoGate, Inc.  Berlin Heights., Ohio.  www.AutoGate.com

Shield Model M50 VP-CB.  ASTM F2656 M50/P1

Shield Model M30 VP-CB.  ASTM F2656 M30/P1

Shield Model Shallow Foundation, M30 VP-SF-CB.  ASTM F2656 M30/P1

BARRIER CONSTRUCTION

Materials:

High strength synthetic ropes – Multiple bundles of braided rope continuous lengths in tension within integral rope aluminum housing.

Ropes do not require tensioning on site.

Solid high strength steel round pins integral to aluminum rope housing.

Aluminum Assembly Framing:

Plate, Shapes and Bar:  ASTM B221, alloy 6061-T6 or 6063-T6.

Extrusions:   Alloy and temper 6063-T6 except formed elbows shall be 6063-T4:

Round Aluminum Pipe:  Standard weight extruded structural aluminum pipe, alloy 6063-T6, mill finish, complying with ASTM B429.

Threaded Fasteners:

All exterior screws, bolts, nut and washers shall be 300 Series non-magnetic stainless steel.

Provide lock washers or other locking devices such as deformed thread lock or nylon locking nuts at all bolted connections.

.

Include any applicable requirements for fencing material if not included in the line fence specification or simply reference the applicable section of the specifications.

Infill panels: Refer to Section __ _____.

Fabrication:

Fabricate Barrier Arm perimeter frames of gates from aluminum sheeting and tubing.  Assemble gate frames by welding at corners.  Infill gate frames with panels to match adjacent fence panels of [chain link fabric] [aluminum square tube pickets] with top treatments of [barb wire] [crush top] [flat top].

Configuration:  Size and space members in compliance with applicable codes.  All gate framing members shall be unspliced single pipe or tube length. Tighten all fasteners so that completed railing is rigid and free of play at joints and component attachments.

Welding:  Make exposed joints butt tight, flush, and hairline. Continuously seal joined members by continuous welds.

Fabricated frame and infill fabric:  Epoxy coated or plain to match fence line color.

Barbed wire assemblies:  Extend gate post and vertical frame members 12 inches above top of chain-link fabric.

OPERATOR(S)

Provide barrier operator system, including operator, field required batteries, external contact sensing equipment [and]  [or] external non-contact sensing equipment.

Drop Arm Speed:  Fully open to fully closed and fully closed to open not greater than 12-14 seconds.

Frequency of Use:   Continuous duty.

In case of power failure battery system using (2) Group 24, 12 volt, Marine Starting, sealed batteries will operate gates for up to 24 hours and then reset operator to normal operation when power resumes. Note AutoGate does not provide batteries; batteries are to be supplied by the Subcontractor installing the system.

Battery Powered Back Up DC Drive System:  Operator to run on 24 Volt DC current stand-by battery system with built-in battery maintainer  "over-charge"  protection.

Provide two (2) 12v batteries, complying with operator manufacturer’s recommendation.  AutoGate recommends Group 24, Marine Starting, Sealed batteries.

Power supply to batteries:  120VAC  (15 amp).

Barrier Operator Enclosure: Fabricate operator frame from steel tubing and sheet metal.   Continuous seal weld all frame seams with welds ground smooth.  Screwed frame members are not acceptable.

All AutoGate operator enclosures are fabricated from galvanealed steel and continuously seal welded prior to finishing to prevent rusting. Select finished color from the standard PPG colors as listed or provide specifics on special colors and paint manufacturers as selected

Frame:  2” Sq., 11 Ga. (.120)  Steel Tubing.

Operator Skins:  18 Ga. Galvaneal Sheet.

Mounting Pads:  3”wide x ¾” thick steel flat bar.

Finish:

Operator:  Standard finish of Black, powder coated.  Colors other than black are offered in 2 part spray application.

Drop Arm/Gate and operators [if non-powder coated black] are spray applied in the color of  [White] [Brown] [Green] [Gray] [Custom color________ RAL# or paint sample required for AutoGate to match).

Mechanical Barrier Operator Drive:

Drive Type:  V-belt and worm gear reducers, roller-chain drive.

Motor:  24VDC high torque gear ball bearing motor with hardened steel gears lubricated with synthetic automatic transmission fluid (Rated to -70º F)

Control Circuitry:   Solid state coated control board in an electrical enclosure.  Sealed proximity switches ensure weather and moisture-proof integrity. (Boards tested to –40º F).

            - Control Wiring: 16 & 18 Ga. single conductor. Copper w/electrolytic copper compression terminals tin-plated for maximum corrosion prevention.

Reference appropriate Class in the following paragraph IF REQUIRING UL325 SAFETY STANDARDS TO APPLY TO PROJECT. Class III - Industrial /Limited Access Vehicular Gate Operator: A vehicular gate operator (or system) intended for use in an industrial location or building such as a factory or loading dock area or other locations not intended to service the general public. -or- Class IV - Restricted Access Vehicular Gate Operator A vehicular gate operator (or system) intended for use in a guarded industrial location or building such as an airport security area or other restricted access location not servicing the general public, in which unauthorized access is prevented via supervisions by security personnel.

[Note: Delete if system is not to conform to UL 325]  Barrier Operator System shall conform to UL 325 [Class III] [Class IV] as determined in accordance with ASTM F2200.  IF APPLICABLE TO PROJECT ONLY.  VERY UNCOMMON TO MOST ACTIVE BARRIER PROJECTS

Type A Entrapment Sensing Device - Operator shall have inherent motor current sensors as part of the gate operator system.  Type A shall be constructed such that it may not be removed or bypassed.

Operator shall have provision for connection of Control System and for connection of [or supplied with] External Entrapment Protection Device specified hereinafter.

External Entrapment Protection Devices:  Provide the following external entrapment protection device(s) as appropriate for the specific site conditions to protect against all potential entrapment zones.

The same type of device shall not be utilized for both the primary and the external entrapment protection means. Use of a single device to cover both the opening and closing directions is in accordance with the requirement; however a single device is not required to cover both directions. A combination of one Type B1 for one direction and one Type B2 for the other direction is the equivalent of one device for the purpose of complying with the requirements of either the primary or secondary entrapment protection means.

Photo Beams Type B1 - Non-contact sensor (photoelectric sensor or the equivalent);

Safety Edges (Contact Edges) Type B2 - Contact sensor (edge device or the equivalent).

Operator Settings & Output

Provide adjustable timer (adjustable from 0 – 60 seconds) for barrier closure.

Provide maximum run timer.

Provide barrier open and barrier closed output

Provide control of traffic light [other accessory]

Operator Options [Optional, delete items not desired]:

Provide surge and spike protection (Field Supplied).

Provide [siren, strobe light, traffic light, etc.]

Provide LED lights on Drop Arm

Provide reflective tape on Barrier Arm [MUTCD, SDDCTEA, etc. compliant].

CONTROL SYSTEMS

Include basic position control system (open/close) unless more sophisticated controls are specified in a separate section. Any dry contact type control system is compatible with the AutoGate operator.

Operation control system:  Remote-control stations, safety devices, and weatherproof enclosures; coordinate electrical requirements with building electrical system.

Control Station (located remotely from barrier system):  Constant [or] Momentary-contact [Two Position (Open/close) or Three Position (Open/Close/Stop)].  Provide key switch to lock out open and close buttons. [See Specification Section ____ for product information and use]

Or

Barrier Operation control systems are specified under Section __ ____.

Card Reader:  Functions only when authorized card is presented.

2.	Digital Keypad Entry Unit:  Multiple - [programmable] code

3.         Access Control System of [Manufacturer_______, Model______]

4.	Radio Control:  Digital system consisting of code-compatible universal receiver                                      for each barrier.

5.	Provide emergency stop button in an outdoor weathertight enclosure..

6.	Vehicle Loop Detector.

7.	Vehicle Presence Detector.

C.       Sequence of Operation

1.      Sequence of operation will include but shall not be limited to the following:

a.  Barrier System Sequencing

b.  Vehicle loop detector functions

c.   Entrapment protection devices

d.  Drop Arm/Gate functions

e.  Traffic Lights

f.   Warning Lights / Strobes / Audible devices

g.   All “other” equipment connected to or controlled by the system

2.    Site access controls, facility access controls, fire alarms, PLCs (programmable logic     controls and associated integration of each are the responsibility of the installer to coordinate with other contractors, facility personnel, authorities having jurisdiction, and communicate any questions or concerns with AutoGate.

ACCESSORIES

Provide [audible] [and] [or] [visible] warning device to signal both directions when the barrier is opening and closing.

Provide 8” Traffic Lights [2 color, 3 color, Red/Yellow/Green]

Provide warning signs on each side of barrier [See Specification Section __].  Drilling into Drop Arm is not permitted and will void the warranty.

Optional Items (Site or request dependent, consult AutoGate for regional needs):

Gearmotor Heater:  Provide thermostatically controlled electric heat tape to maintain critical components operational.  [Contact AutoGate to determine if project location requires gear motor heater.]

Extreme Cold Weather Kit: Provide an insulated Operator Cabinet and include a thermostatically controlled electric space heater with integral circulating fan.  [Contact manufacture to determine if project location warrants this kit]

SETTING MATERIAL

Ready-mixed concrete complying with ASTM C94:  Normal-weight concrete [air entrained] 3000-psi 28 days compressive strength, 3-inch slump, and aggregate.

Portland cement:  ASTM C150, Type I.

Aggregates:   ASTM C33, 1-inch maximum size.

Reinforcing Bars:  ASTM A615.

Service and control conduit:  Rigid Schedule 40 PVC embedded in concrete.  All other conduit and wiring as specified in Division [26] [16].

Expansion Bolts:   Threaded or wedge type; galvanize ferrous castings, ASTM A47 malleable iron or ASTM A27 cast steel.

EXECUTION

EXAMINATION

Installer's Examination:  Examine conditions under which construction activities of this section are to be performed for compliance with all specified criteria.

Submit written notification to Specifier/Owner and system manufacturer if any conditions that are unacceptable.

Beginning installation/erection constitutes installer's acceptance of initial conditions.

ELECTRICAL SERVICE & CONTROLS

Provide all power and control wiring required for the work in accordance with the applicable provisions of Division [26] [16] and NEC 70.

Perform all trenching and backfilling associated with this Section.  Conduit shall be direct buried except under areas of vehicular traffic where it shall be reinforced concrete encased.

Grounding system: All equipment and branch circuits shall be grounded.  Provide driven ground rod at service.   Provide separate ground wire in all branch circuits.

PADS & BOLSTERS

Foundations:  Construct pads and Bolster foundations as indicated on the drawings with top of concrete flat and level.

Excavation:

Prepare the work site and locate general area for barrier installation by surveying or other suitable measurements.

Locate concrete foundations for operator base on firm, undisturbed soil.

Bolster Excavation: Locations to be in accordance with manufacturers site drawings. Foundation pit to be excavated an additional depth to allow for a concrete Leveling Pad (See manufacturer site drawings for depth and leveling pad information).  Leveling Pad to be completed prior to placement of Bolsters in foundation pit and pouring of concrete foundation which surrounds Bolsters.

Coordinate with electrician for all needed conduit between operator and yoke end bolster.  Ensure Yoke end bolster accessories have necessary power and control conduits for applicable accessories.

Vibrate or tamp concrete for consolidation.  Finish top of foundations, smooth and even.   Cure concrete 72 hours before place operator.

Fasteners:  Install operators with expansion bolts provided by the barrier system manufacturer.

OPERATOR INSTALLATION

Install units in accordance with the manufacturer's instructions and drawings.

Operator Expansion Bolt Mounting:  Anchor through base plates to concrete substrate.

Install all loose shipped operator lower panels and guarding per manufacturer instructions.

External Entrapment Protection Device: Installing contractor shall be responsible for providing external entrapment protection devices as appropriate for the specific site conditions to protect against all potential entrapment zones.   Proper operation of these safety devices shall be verified and training as to the operation and maintenance of these devices for the users and owners shall be documented.

BARRIER INSTALLATION

If shipped unassembled, connect drop arm to operator arm in accordance with manufacturer’s instruction.

Install barrier so that it is plumb and level when fully closed within the following tolerances:

Maximum misalignment from true position:  1/4 inch (6.0 mm).

Maximum misalignment between adjacent separated members:  1/8  inch (3.0 mm).

ADJUSTING

Adjust and lubricate operating components for smooth, accurate operation free of binding and racking.

START-UP AND DEMONSTRATION

Manufacturer's Service Representative:  Provide at least 2 hours of manufacturer's representatives time for start-up and initial operation.  Make a final check of each barrier system operation, with Owner's personnel present, immediately before date of substantial completion.

Instruct Owner's personnel in proper use, operations, and maintenance of the barrier system.  Review emergency provisions, including procedures to be followed if drop arm does not close or open.  Train Owner's personnel in normal procedures to be followed in checking for sources of damage or operational failures or malfunctions.

Determine that control systems, entrapment sensing devices, and operating devices are functioning properly.

[Adjust time control systems/clocks/etc. for periods required and as directed.]

CLEANING AND PROTECTION

Remove dust or other foreign matter from component surfaces; clean finishes in accordance with manufacturer's instructions.

Clean units in accordance with the manufacturer's instructions.

Protection:  After installation, protect installed work until project completion.

Ensure that finishes and structure of installed systems are not damaged by subsequent construction activities.

If minor damage to finishes occurs, repair damage in accordance with manufacturer's recommendations; provide replacement components if repaired finishes are unacceptable to Architect.

Document any installation notes or comments.  Submit to site personnel, Architect, and AutoGate.

Photograph installed Barrier System(s) from multiple angles and positions.  Submit to site personnel, Architect/Engineer, and AutoGate.

END OF SECTION 34 75 13.16